The Colt Smokemaster SM-ST fixed smoke curtain prevents the movement of smoke and heat from one area to another in a fire by channelling or containing the smoke and heat. It conforms to EN 12101-1 and is available with a D120, DH60, or DH120 rating.  Fixed smoke curtains provide protection from the adverse effects of smoke movement for most kinds of industrial and commercial buildings. The Smokemaster SM-ST fixed smoke curtain consists of a fabric material which is held within a series of angle pieces and thereby clamped. At the bottom of the cloth there is a weight to keep the cloth taut, ensuring that the curtain remains taut and reduces the amount of deflection through air currents.

Products manufactured by the Colt Group are distributed by Fire Curtain Technologies. Before including this specification in your Project Manual, delete types and options not required for your project.  For more information, please visit our website ww.firecurtaintechnologies.com or call 585-412-2179.

SECTION 083342

FIXED SMOKE CURTAINS

(SMOKEMASTER SM-ST)

GENERAL

SUMMARY

Work Included: Provide labor, materials and equipment necessary to complete the work of this Section, including but not limited to the following:

Fixed smoke curtains.

Related Work: The following items are not included in this Section and are specified under the designated Sections:

Division 23 - Heating, Ventilating and Air Conditioning for smoke control systems that are a part of mechanical equipment.

SUBMITTALS

Product Data: Submit manufacturer’s product data.

Shop Drawings: Submit shop drawings including plans, elevations, sections, details, and attachment to adjacent Work.

Warranty: Submit executed copy of manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer: A minimum of 5 years experience manufacturing similar products.

Installer: A minimum of 2 years experience installing similar products.

PROJECT CONDITIONS

Field Measurements: For custom sized units, verify openings by field measurements before fabrication and indicate measurements on Shop Drawings.

WARRANTY

Warranty: Provide manufacturer’s standard limited warranty.

PRODUCTS.

MANUFACTURER

Basis-of-Design Manufacturer: The Colt Group as distributed by Fire Curtain Technologies, 5711 Thomas Road, Canandaigua, NY. 14424. Tel: 585-412-2179 http://firecurtaintechnologies.com/

FIXED SMOKE CURTAINS

Fixed Smoke Curtains: Smokemaster SM-ST Fixed Smoke Curtains by the Colt Group, as distributed by Fire Curtain Technologies.

Description: Fixed smoke curtain, to prevent the movement of smoke and heat from one area to another in a fire.

Dimensions/Size Range: Provide size suitable for project requirements; refer to the Drawings. Overall curtain lengths for single units are available from 59” (1500mm) to an unlimited length, and drops are available from 20” (500 mm) to 590” (15000mm).

Performance:

Tested to EN 12101-1, and achieves a rating of: D120 1112OF (600OC) for 120 minutes or DH 120 1920OF (1049OC) for 120 minutes.

Designed to withstand hot air and smoke at temperatures up to 1112OF (600OC) for 120 minutes once only.

Fabric Fire Resistance to Fire: A2-s1,d0 when tested in accordance with EN 13501-1.

Compliance: Overall system tested to and in compliance with EN 12101-1 and CE marked. Fabric tested to EN 13501-1.

FABRICATION, GENERAL

Assemble units in factory to minimize field splicing and assembly. Disassemble units as necessary for shipping and handling limitations. Clearly mark units for reassembly and coordinated installation.

Fabricate to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter joints. Include anchors and accessories required for complete assembly.

EXECUTION

EXAMINATION

Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance. Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION.

Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work. Use concealed anchorages where possible.

Form closely fitted joints with connections accurately located and secured.

Restore damaged finishes so no evidence remains of corrective work.

ADJUSTING AND CLEANING

Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION