The Colt FM1 is an electronically-operated fire curtain system that seals off an area which is on fire, thereby preventing fire from moving from one area to another. It conforms to EN 1634-1 and provides protection for a pre-defined period.

Products manufactured by the Colt Group are distributed by Fire Curtain Technologies. Before including this specification in your Project Manual, delete types and options not required for your project.  For more information, please visit our website www.bilco-colt.com or call 585-412-2179.

SECTION 083344

AUTOMATIC FIRE CURTAINS

(COLT FM1 Fire Curtain)

GENERAL

SUMMARY

Work Included:  Provide labor, materials and equipment necessary to complete the work of this Section, including but not limited to the following:

Automatic fire curtains.

Related Work: The following items are not included in this Section and are specified under the designated Sections:

Division 23 - Heating, Ventilating and Air Conditioning for fire control systems that are a part of mechanical equipment.

Division 26 - ELECTRICAL for fire control systems that are a part of electrical equipment.

SUBMITTALS

Product Data:  Submit manufacturer’s product data.

Shop Drawings: Submit shop drawings including plans, elevations, sections, details, and attachment to adjacent Work.

Warranty:  Submit executed copy of manufacturer’s standard warranty.

QUALITY ASSURANCE

Manufacturer: A minimum of 5 years experience manufacturing similar products.

Installer: A minimum of 2 years experience installing similar products.

PROJECT CONDITIONS

Field Measurements: For custom sized units, verify openings by field measurements before fabrication and indicate measurements on Shop Drawings.

WARRANTY

Warranty: Provide manufacturer’s standard limited warranty.

PRODUCTS.

MANUFACTURER

Basis-of-Design Manufacturer: The Colt Group as distributed by Fire Curtain Technologies, 5711 Thomas Road, Canandaigua, NY. 14424. Tel: 585-412-2179 http://firecurtaintechnologies.com

AUTOMATIC FIRE CURTAINS

Automatic Fire Curtains: FM1 Fire Curtains by Colt Group, as distributed by Fire Curtain Technologies.

Description: Electrically operated automatic fire curtain, which seals off an area which is on fire, thereby preventing fire from moving from one area to another. The curtain falls under gravity in a controlled manner to a predetermined level in a fire situation or on loss of power. Curtain drop shall be full floor to ceiling height for fire containment.

Dimensions/Size Range: Provide size suitable for project requirements; refer to the Drawings. Overall curtain lengths for single units are available from 40” (1000mm) to 197” (5000 mm), and drops are available from 20” (500mm) to 197” (5000mm). A requirement above these dimensions will be met by installing either double horizontal or double vertical units. Double vertical and double horizontal units are unlimited in length and drops are available from 20” (500mm) to 236” (6000mm) depending upon curtain configuration.

Type: Shall be [select one: Single units (type SI) or Double vertical (type DV) units, where continuous runs with overlapped fabric to form a continuous barrier are required or Double horizontal (type DH) units, where there is a premium on space under the ceiling].

Bottom Bar Type: Shall be [select one: Industrial bottom bar (fabric loop) or Comfort bottom bar (aluminum profile).]

Fabric Type: Shall be [select one: E 60 heat stabilized fabric or E 120 heat stabilized fabric with a stainless steel inlay, achieving 120 minutes fire integrity, with a EW 30 reduced radiation class or E 180 stabilized fabric with a stainless steel inlay, achieving 180 minutes fire integrity, with a EW 30 reduced radiation class.]

Control Type: Shall be [select one: Simple control box with switches and an indication lamp or smoke detector connected directly to this control box or a local control box to be connected to the central fire detection system with a voltage free contact or battery back-up to retain the curtain in its retracted position for a set period if there is a main failure.]

Performance:

EN 1634-1 "Testing of non-load bearing construction elements"

EN 13501-2 "Fire classification of construction products and building elements."

Tested to EN 1634-1 and classified as E60-C, E120-C or E180-C in accordance with EN 13501-2:2007, thereby achieving an integrity rating for either 60, 120 or 180 minutes.

Fabric Fire Resistance to Fire: E 60, E 120 and E 180 fabrics achieve the building classification A2 S1 d0 to EN13501-2: 2007 ("Fire classification of construction products and building elements"). E120-C and E180-C fabrics achieve a EW 30 class in accordance with EN 13501-2, which demonstrates that they re-radiate only a limited amount of heat.

Compliance: Successful continuous performance test (10,000 cycles) in accordance with DIN 4102-18.

FABRICATION, GENERAL

Assemble units in factory to minimize field splicing and assembly.  Disassemble units as necessary for shipping and handling limitations. Clearly mark units for reassembly and coordinated installation.

Fabricate to fit in openings of sizes indicated, with allowances made for fabrication and installation tolerances, adjoining material tolerances, and perimeter joints.  Include anchors and accessories required for complete assembly.

EXECUTION

EXAMINATION

Examine substrates and openings for compliance with requirements for installation tolerances and other conditions affecting performance. Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION.

Install products in strict accordance with manufacturer’s instructions and approved submittals.  Locate units level, plumb, and in proper alignment with adjacent work. Use concealed anchorages where possible.

Form closely fitted joints with connections accurately located and secured.

Test operable units for proper function and adjust until proper operation is achieved.

Restore damaged finishes so no evidence remains of corrective work.

ADJUSTING AND CLEANING

Clean exposed surfaces using methods acceptable to the manufacturer which will not damage finish.

END OF SECTION