Section 08 3483

Elevator door smoke containment system

PART 1 - General

## Summary

### Section Includes: Smoke detector activated elevator door smoke containment screen and control system designed to provide a tight-fitting, smoke- and draft-control assembly.

### Products Supplied But Not Installed Under This Section:

#### End-of-line diode (3.9V, 2W). Installed at smoke detector to monitor the circuit.

### Related Sections:

#### 09 2200(Non-Load Bearing Wall Framing: Metal backing in housing mounting area.

#### 09 9100(Paints: Field painting of specified components; repainting of existing field painted elevator door frames.

#### 28 3000(Detection and Alarm: Provision of smoke detectors.

#### 14 2100(Electric Traction Elevators.

#### 14 2400(Hydraulic Elevators.

#### Division 26 Sections for 120V AC and control circuit power including conduit, boxes, conductors, wiring devices, and emergency power.

## References

### ASTM A240/240M ( Standard Specification for Heat Resisting Chromium and Chromium-Nickel Stainless Steel Plate, Sheet and Strip for Pressure Vessels.

### CCRR-1059 Intertek Code Compliance Research Report

### NFPA Codes and Standards:

#### 70 ( National Electrical Code.

#### 105 ( Recommended Practice for the Installation of Smoke-Control Door Assemblies.

#### 72-2002 and 2007 – National Fire Alarm Code

### International Building Code

#### 2003.

#### 2006

#### 2009

#### 2012

#### 2015

#### 2018

### UL Standards:

#### 268 ( Smoke Detectors for Fire Protective Signaling Systems.

#### 508 ( Industrial Control Equipment.

#### 864 ( Control Units for Fire Protective Signaling Systems.

#### 1784 ( Air Leakage Tests for Door Assemblies.

#### ASTME 84 – Fabric Test for Door Assemblies.

## Submittals

### Reference Section 01 3300(Submittal Procedures; submit following items:

#### Product Data.

#### Shop Drawings: Include door width and height, jamb width, jamb and head projection, screen width, mounting height, and housing width. Show and identify related work performed under other sections of the specifications.

#### Quality Assurance/Control Submittals:

##### Qualifications:

###### Proof of manufacturer qualifications.

###### Proof of Installer qualifications.

##### Certifications: Copy of specified items.

##### Manufacturer’s installation instructions and testing procedures

## Closeout Submittals

### Comply Section 01 7700(Closeout Submittals; submit following items:

#### Operation and Maintenance [Manual]

#### Manufacturer’s Warranties

## Quality Assurance

### Overall Standards:

#### Manufacturer shall maintain a quality control program in accordance with ICC-ES Acceptance Criteria for Smoke Containment Systems Used with Fire-resistive Elevator Hoistway Doors and Frames (AC77, Section 3.1.1), dated June 2013.

### Qualifications:

#### Manufacturer Qualifications: Minimum 10 years experience in producing smoke containment systems.

#### Installer Qualifications: Factory trained by manufacturer.

### Certifications and other listings:

#### California Department of Forestry and Fire Protection and Office of the State Fire Marshal Listing.

#### OSHPD Anchorage Pre-Approval OPM-0371-13

### Manufacturer’s CCRR-1059 Intertek Code Compliance Research Report

### showing compliance in accordance with:

##### ICC-ES AC77

##### UL standard 1784

##### ASTME 84

##### NFPA 105

##### IAS (IAS is a trademark of International Accreditation Service) Accredited Testing Laboratory Labels for UL Standard 1784

##### IAS (IAS is a trademark of International Accreditation Service) Accredited Testing Laboratory Labels for UL Standard 864

### Pre-Installation Meeting:

Include painting sub-contractor in following paragraph if new or existing elevator door frames or auxiliary rails will be field painted.

#### Schedule and convene a pre-installation meeting prior to commencement of field operations with representatives of the following in attendance: Owner, Architect, General Contractor, smoke containment system sub-contractor, painting sub-contractor, and electrical sub-contractor.

#### Review substrate conditions, requirements of related work, installation instructions, storage and handling procedures, and protection measures.

#### Keep minutes of meeting including responsibilities of various parties and deviations from specifications and installation instructions.

## Delivery, Storage, and Handling

### Reference Section 01 6600(Product Storage and Handling Requirements.

### Follow manufacturer’s instructions.

## Warranty

### Provide manufacturer’s standard one year warranty.

### Maintenance and Testing:

#### Perform minimum semi-annual maintenance and testing on each smoke containment system as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.

#### Provide test documentation.

# Products

## Manufacturer

### Smoke Curtain GX

### Manufacturer: Stöbich Brandschutz, Pracherstieg 6, 38644 Goslar / Germany

Distributed by Fire Curtain Technologies; Canandaigua, NY 14424; Tel: 585-412-2179; Email: info@firecurtaintech.com, www.firecurtaintechnologies.com

### Label each smoke containment system with following information:

#### Manufacturer’s name.

#### Maximum leakage rating at specified pressure and temperature conditions.

#### Label of quality control agency.

## Performance Requirements

### Air Leakage:  Not to exceed 3 cfm (0.001416 m3/s) per sf of door opening at 0.1 in (25 Pa) water pressure differential at ambient temperature and 400 degrees F (204 degrees C) tested per IBC 2006, 2009, 2012, 2015 and 2018.

## Components

### Screen:

#### PEEK Foil: thickness: 0.006mm (6µm)

#### Material: polyetherketone

#### Temperature behavior: 649°F /343°C

#### Magnetic Strips: Flexible strips attached to longitudinal edges of fabric

### Housing: 18 gage, powder coated, steel container with door. Housings are up to 12feet in length and max. 12 feet drop length curtain.

### Auxiliary Rails:

#### Material: 12 gage ASTM A 240/240M, Type 430, ferritic stainless steel.

#### Size: 2.36 inches (60 mm) wide; 1 inch (25 mm) deep, depth beyond face of elevator door frame, as shown in Shop Drawings.

#### If Painting of rails is required, Paint must be heat resistant to 302 degrees f (150 degrees c) and be spray applied, maximum 5 mils (.13 mm) thick including primer

#### Auxiliary rails that are non-Ferrous are NOT ALLOWED at the area of the Smoke Curtain GX magnetic strips will contact.

### Rewind Motor:

#### Gravigen motor, fail safe operation.

#### Control box: 120V AC/60Hz / 24V DC.

#### Motor: 24V DC

### Control System:

#### Comply with UL Standard No. 864.

#### GX control box. Battery backup optional.

#### Hold open time with optional battery backup: 20 minutes.

### Release Mechanism: IAS (IAS is a trademark of International Accreditation Service) Accredited Testing Laboratory Labels for UL Standard 864.

### Hold open time curtain in case of power loss in the building: 20 minutes.

### Optional Wall Switch: Switch to rewind curtain into housing.

# Execution

## Examination

### Examine substrates upon which work will be installed.

#### Verify related work performed under other sections is complete and in accordance with Shop Drawings.

#### Verify wall surfaces and elevator door frames are acceptable for installation of smoke containment system components.

#### Verify existing field painted elevator door frames to be used for screen adherence have been repainted in accordance with smoke containment system manufacturer’s instructions or they have the original factory paint.

### Coordinate with responsible entity to perform corrective work on unsatisfactory substrates.

### Commencement of work by installer is acceptance of substrate.

## INSTALLATION

Manufacturer’s installation instructions cover procedures for normal installation and assume the design and detailing complies with Stoebich Fire Protection Systems Inc. system requirements. Unusual conditions or variations from Stoebich Fire Protection Systems Inc. system requirements should be added to this article.

### Install smoke containment system components in accordance with manufacturer’s installation instructions.

## Field Quality Control

### Field Test: Follow manufacturer’s cycle test procedures.

#### Notify Owner’s Representative, local Fire Marshal, alarm sub-contractor and [elevator sub-contractor] [elevator service company] minimum one week in advance of scheduled testing.

#### Complete maintenance service record.

## Demonstration

### Demonstrate required testing and maintenance procedures to Owner’s Representative.

### Maintenance and Testing:

#### Perform minimum semi-annual maintenance and testing on each smoke containment system as required by the manufacturer’s warranty, code agency evaluation reports, and as required by local authority having jurisdiction.

#### Retain permanent record of tests.

### Future Painting: Paint elevator door frame and/or auxiliary rails in accordance with Operation and Maintenance Manual.

### Qualified Stoebich Fire Protection Systems Inc. Inspector assesses unit(s) after exposure to a fire event.

End of Section